SECTION 23 51 00
BREECHINGS, CHIMNEYS, AND STACKS

PART 1 GENERAL

1.1 SECTION INCLUDES

A. Factory-built venting systems for Category II, III, and IV gas-fired appliances.
1.2 RELATED SECTIONS

A. Section 22 33 00 – Electric Domestic Water Heater
B. Section 23 52 00 – Heating Boilers
1.3 REFERENCES

A. ANSI Z223.1 (NFPA 54) – The National Fuel Gas Code

B. ASHRAE – Handbook, equipment Volume, Chapter “Chimney, Gas, Vent, and Fireplace Systems”

C. NFPA 211 – Standard for Chimneys, Fireplace, Vents, and Solid Fuel – Burning Appliances

D. SMACNA – HVAC Duct Construction Standards – Metal and flexible

E. UL 1738 – Standard for Venting Systems for Gas-Burning Appliances Categories II, III, and IV
1.4 DEFINITIONS

A. Category II Appliance: Appliance operating with non-positive vent static pressure and flue gas temperatures capable of producing condensate.
B. Category III Appliance: Appliance operating with positive vent static pressure and flue gas temperatures that do not produce significant condensate.

C. Category IV Appliance: Appliance operating with positive vent static pressure and flue gas temperatures capable of producing condensate.
D. Condensate: Liquid formed from the cooling of combustion products within the venting system.

E. Positive Pressure Vent: Venting system designed and listed to contain flue gases under positive internal pressure.

1.5 SUBMITTALS

A. Submit shop drawings under provisions of Section 01330.

B. Submit shop drawings indicating general construction, dimensions, support, and layout of breechings. Where factory built units are used, submit layout drawings including plan view and elevations.

C. Submit product data under provisions of Section 01330.

D. Submit product data indicating factory built chimneys, including dimensional details of components and flue caps, dimensions and weights.

E. Submit manufacturer’s installation instructions under provisions of Section 01330.

1.6 QUALIFICATIONS

A. Manufacturer: Company specializing in the manufacture of products specified in this Section with minimum ten years’ documented experience.

1.7 REGULATORY REQUIREMENTS

A. Conform to applicable ANSI Z223.1 code (NFPA 54) for installation of natural gas burning appliances and equipment.

PART 2 PRODUCTS

2.1 MANUFACTURERS

A. Van-Packer Co., Inc.
B. Or equal

2.2 CATEGORY II, III, AND IV VENTING SYSTEMS
A. Provide double wall metal vents, tested to UL 1738 and UL listed for use with category II, III, and IV gas fired appliances.

B. Vent shall be rated for up to 550° F continuous fire and 40” water column positive pressure.
C. Fabricate with (□1, □2, □3, □4)-inch minimum (□ Air Space, □ Mineral Wool Insulation) between walls. Construct inner liner of 24 gauge minimum corrosion resistant (□ VP1738™ stainless steel, □ VP1738A™ stainless steel, □ AL29-4C stainless steel, □ 316L Stainless Steel) in accordance with UL listing. Construct outer shell of 24 gauge minimum (□ aluminized steel, □ type 430 stainless steel, □ type 304 stainless steel, □ type 316 stainless steel).
D. Vent shall be listed for 2” clearance to combustibles and 0” clearance to non-combustibles.
E. Provide all required accessories for a complete system each bearing factory applied UL Label, including but not limited to supports, appliances connectors, drain fittings, and terminations.
F. Provide condensate drains at locations indicated by the manufacturer and as required to prevent accumulation of condensate within the venting system.

1.8 WARRANTY

A. Manufacturer shall provide a Lifetime Warranty against defects in material and workmanship for all factory-built exhaust system components supplied under this Section.

B. Warranty shall apply to the original installation and cover repair or replacement, at the manufacturer's discretion, of components determined to be defective under normal operating conditions and proper use.

C. Warranty shall not apply to damage resulting from:

a. Improper installation.

b. Improper operation or misuse.

c. Corrosion resulting from operating conditions outside the design parameters of the system.

d. Physical abuse, modification, or unauthorized repairs.

e. Failure to properly support, maintain, inspect, or clean the exhaust system in accordance with manufacturer requirements.

D. Exterior components exposed to weather shall be properly sealed, protected, and maintained in accordance with manufacturer recommendations.

E. Warranty documentation shall be provided with project submittals upon request.

PART 3 EXECUTION

3.1 INSTALLATION

A. Install in accordance with manufacturer’s instructions.

B. Install in accordance with recommendations of ASHRAE – Handbook, Equipment Volume, Chapter “Chimney, Gas, Vent, and Fireplace Systems” and ANSI Z223.1, (NFPA 54).
C. Install breechings with minimum of joints. Align accurately at connections with internal surfaces smooth.

D. Install breechings from the building structure using suitable ties, braces, hangers, and anchors to maintain alignment and prevent buckling. Horizontal supports shall be spaced at intervals not exceeding 10 feet.
E. Support vertical venting systems with lateral bracing to adjacent structural surfaces or at floor penetrations. The distance from the stack termination to the first lateral brace shall not exceed 10 feet. Additional lateral bracing shall be provided at intervals not exceeding 20 feet for all diameters. Refer to SMACNA HVAC Duct Construction Standards for equivalent duct support configurations and sizes.
F. Install concrete inserts for supporting vent in coordination with formwork.

G. Pitch venting system in accordance with manufacturer recommendations to permit proper condensate drainage.

H. Maintain UL listed minimum clearances from combustibles.

I. Inner pipe joints shall be sealed by use of Vee Bands and Silicone Sealant.

J. Assemble pipe and accessories as required for complete installation.

K. Chimneys extending above roof surfaces must terminate as required by local code, or as required in NFPA 211.

L. Level and plumb chimneys.

M. Clean breeching and chimney during installation, removing dust and debris.

N. At appliances, provide slip joints permitting removal of appliances without removal or dismantling of breechings or chimneys.

O. All parts exposed to the outer atmosphere that are fabricated from aluminized steel shall be protected by a minimum of one base coat and one finish coat of paint, such as Rust-O-Leum Clean Metal Primer and appropriate top coat, or equivalent. Paint to be supplied and applied by installing contractor.

END OF SECTION

SpecCS155752009.doc


