SECTION 23 51 00
BREECHINGS, CHIMNEYS, AND STACKS

PART 1 GENERAL

1.1 SECTION INCLUDES

A. Manufactured chimneys for gas and oil fired equipment

1.2 RELATED SECTIONS

A. Section 22 33 00 – Electric Domestic Water Heater
B. Section 23 52 00 – Heating Boilers
1.3 REFERENCES

A. NFPA 31 – Standard for the Installation of Oil Burning

Equipment

B. ANSI Z223.1 (NFPA 54) – The National Fuel Gas and LP Code

C. NFPA 58 – Liquefied Petroleum Gas Code
D. NFPA 31 - Standard for the Installation of Oil-Burning Equipment
E. NFPA 37 - Installation and use of stationary combustion engines and gas turbines
F. ASHRAE – Handbook, equipment Volume, Chapter “Chimney, Gas, Vent, and Fireplace Systems”

G. NFPA 211 – Standard for Chimneys, Fireplace, Vents, and Solid Fuel – Burning Appliances

H. SMACNA – HVAC Duct Construction Standards – Metal and flexible

I. UL 103 – Standard for Factory Built Low Heat Chimney

J. UL 641 – Standard for Type L Low Temperature Venting Systems

K. UL 2561 – Standard for 1400 Degree Fahrenheit Factory-Built Chimneys

L. NFPA 85 – Boiler and Combustion Systems Hazards Code
1.4 DEFINITIONS

A. Breeching: The conduit conveying flue gas from the appliance to the chimney.

B. Chimney: A structure containing one or more vertical or nearly vertical passageways for conveying flue gases to the outside.

C. Exhaust Stack: A flue gas conveying system intended for use only with certain gas, liquid, or pellet fuel-fired appliances that do not produce flue gas outlet temperatures higher than a value specified in the listing vent standards.

D. Vent Connector: The pipe that connects a fuel-burning appliance to a gas vent or Type L vent.

E. Venting System: A continuous, open passageway from the flue collar or draft hood of a fuel-burning appliance to the outside atmosphere for the purpose of removing flue gases.

F. Termination: The final discharge component of the exhaust system, including but not limited to velocity cones, rain caps, open terminations, and specialty exhaust nozzles.
1.5 SUBMITTALS

A. Submit shop drawings under provisions of Section 01330.

B. Submit shop drawings indicating general construction, dimensions, weights, support, and layout of breechings. Where factory built units are used submit layout drawings including plan view and elevations.

C. Submit product data under provisions of Section 01330.

D. Submit product data indicating factory built chimneys, including dimensional details of components and flue caps, dimensions and weights.

E. Submit manufacturer’s installation instructions under provisions of Section 01330.

1.6 QUALIFICATIONS

A. Manufacturer: Company specializing in the manufacture of products specified in this Section with minimum ten years documented experience.

1.7 REGULATORY REQUIREMENTS

A. Conform to applicable ANSI Z223.1 code for installation of natural gas burning appliances and equipment.

B. Conform to applicable NFPA 58 code for Liquefied Petroleum Gas.

C. Conform to applicable NFPA 31 code for Standard for the Installation of Oil-Burning Equipment.

D. Conform to applicable NFPA 37 code for Installation and use of stationary combustion engines and gas turbines.

E. Conform to applicable NFPA 211 code for Standard for Chimneys, Fireplace, Vents, and Solid Fuel – Burning Appliances

1.8 WARRANTY

A. Manufacturer shall provide a Lifetime Warranty against defects in material and workmanship for all factory-built exhaust system components supplied under this Section.

B. Warranty shall apply to the original installation and cover repair or replacement, at the manufacturer's discretion, of components determined to be defective under normal operating conditions and proper use.

C. Warranty shall not apply to damage resulting from:

a. Improper installation.

b. Improper operation or misuse.

c. Corrosion resulting from operating conditions outside the design parameters of the system.

d. Physical abuse, modification, or unauthorized repairs.

e. Failure to properly support, maintain, inspect, or clean the exhaust system in accordance with manufacturer requirements.

f. Backfire-related damage where manufacturer-required Pressure Relief Valves (PRVs) have been omitted from the system design.

D. Exterior components exposed to weather shall be properly sealed, protected, and maintained in accordance with manufacturer recommendations.

E. Warranty documentation shall be provided with project submittals upon request.

PART 2 PRODUCTS

2.1 MANUFACTURERS

A. Van-Packer Co., Inc.

B. Jeremias
C. DuraVent
D. Hart & Cooley

E. Or equal

2.2 DOUBLE WALL METAL STACKS

A. Provide factory-built double-wall insulated chimneys for venting gas-fired and oil fired heating appliances. Chimney shall be listed to UL 103, UL 2561, and UL 641; suitable for continuous operation at “1400°F and intermittent operation at 1800°F and as a “Building Heating Appliance Chimney” for continuous operation at 1000°F and intermittent operation at 1400°F and in compliance with NFPA 211.

B. Chimney system shall be listed for negative, neutral and positive pressure operation up to 60 inches water column.
C. All components shall be supplied by a single manufacturer and bear the applicable UL listing label.
D. Fabricate with (□1, □2, □3, □4 inch) minimum (□air space , □Mineral Wool Insulation, □Ceramic Fiber Insulation) between walls. Construct inner liner of 20-gauge for sizes 06”ID through 36”ID and 18-gauge for sizes 38”ID through 48”ID. Material shall be type (□304 or □316L) stainless steel. Construct outer shell of 24-gauge for sizes 06”ID through 24”ID and 20-gauge for sizes 26”ID through 48”ID. (□Aluminum coated steel, □type 304 stainless steel, □type 316L stainless steel, □ type 430 stainless steel).
E. Provide all required accessories each bearing factory applied UL Label, including but not limited to:
1. Ventilated Roof Penetration: consist of Ventilated Roof Thimble, Flashing, and Counter Flashing. 

2. □Velocity Cone, □Double Cone Rain Cap, □ Open Top Closure, □ Screen Collar Termination.

3. Expansion Joints: Shall be provided where required by the manufacturer’s design calculations and installation instructions.
4. Chimney Drain: Mount downstream of stack tee connection.

5. Chimney Bottom Assembly: Consist of tee fitting, plate support assembly, and end cap with drain.

PART 3 EXECUTION

3.1 INSTALLATION

A. Install in accordance with manufacturer’s instructions.

B. Install in accordance with recommendations of ASHRAE – Handbook, Equipment Volume, Chapter “Chimney, Gas, Vent, and Fireplace Systems,” and ANZI Z223.1, (NFPA 54).

C. Install breechings with minimum of joints. Align accurately at connections with internal surfaces smooth.

D. Install breechings from building structure, rigidly with suitable ties, braces, hangers, and anchors to hold to shape and prevent buckling. Support vertical vent at 12 foot spacing, to adjacent structural surfaces, or at floor penetrations. Refer to SMACNA HVAC duct Construction Standards – Metal and Flexible for equivalent duct support configuration and size.

E. Install concrete inserts for supporting vent in coordination with formwork.

F. Pitch breechings with positive slope up from fuel-fired equipment to chimney or stack.

G. Inner pipe joints shall be sealed by use of Vee Bands and Silicone Sealant for flue gas temperatures up to 600(F. and high temperature sealant for flue gas temperatures above 600(F. as outlined in the installation instructions and supplied by the manufacturer.

H. Chimneys extending above roof surfaces must terminate as required by local code, or as required in NFPA 211.

I. Level and plumb chimneys.

J. Clean breeching and chimney during installation, removing dust and debris.

K. At appliances, provide slip joints permitting removal of appliances without removal or dismantling of breechings or chimneys.

L. All parts exposed to the outer atmosphere that are fabricated from aluminized steel shall be protected by a minimum of one base coat and one finish coat of paint, such as series 4200-4300 Heat Resistant paint manufactured by Rust-O-Leum Corporation, or equivalent. Paint to be supplied and applied by installing contractor.

END OF SECTION

SpecDW15575.doc


